## MODBUS_COMMANDS
Modbus references for XR75CX
| R/W | COMMAND
PROBES VALUE
Probe 1 | R | 0301080001 |  |  | CRC
Probe 2 | R | 0301090001 |  |  | CRC
Probe 3 | R | 03010A0001 |  |  | CRC | RTC
Probe R | R | 0301000001 |  |  | CRC
Probe 4 | R | 03010B0001 |  |  | CRC
SET POINT | [5 empty] | ADDRESS 0B00 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
SET R | R | 0306000001 |  |  | CRC |  | Seconds (0-59) | [7 empty] | Minutes (0-59)
CRC
SET | R | 0303760001 |  |  | CRC | ADDRESS 0B01 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
| W | 100376000102 |  |  | CRC |  | hour (0-23) | [7 empty] | DAY WEEK (1: SUN, ..., 7:SAT)
DIGITAL INPUT | [5 empty] | ADDRESS 0B02 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
DI1 | R | 010200000F | 8000 | 8000 | CRC |  | DAY (1-31) | [7 empty] | MONTH (1-12)
DI2 |  | 0102200008 | 0010 | 0010 | CRC
[6 empty] | ADDRESS 0B03 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
DIGITAL OUT | [6 empty] | YEAR( EXAMPLE 2007)
On/Off Out | R | 0102080020 | 00400000 | 00400000 | CRC
Defrost | R | 0102080020 | 00800000 | 00800000 | CRC
Defrost 2 | R | 0102080020 | 00000100 | 00000100 | CRC | SECONDS-MINUTES READING EXAMPLE:
Alarm | R | 0102080020 | 20000000 | 20000000 | CRC
Light | R | 0102080020 | 00000400 | 00000400 | CRC |  | TX: | 01 | 03 | 0B | 00 | 00 | 01 | CRC
Fan | R | 0102080020 | 00000800 | 00000800 | CRC |  | RX: | 01 | 03 | 02 | 1F | 3B |  | CRC
Aux | R | 0102080020 | 00001000 | 00001000 | CRC
Neutral Zone | R | 0102080020 | 00002000 | 00002000 | CRC |  | 1F= SECONDS IN HEX
Cooling | R | 0102080020 | 00004000 | 00004000 | CRC |  | 3B= MINUTES IN HEX
Cooling 2 | R | 0102080020 | 00008000 | 00008000 | CRC
Energy Saving | R | 0102080020 | 00000080 | 00000080 | CRC | SECONDS-MINUTES WRITING EXAMPLE:
STATUS
On | R | 0102000008 | 0001 | 0001 | CRC |  | TX: | 01 | 06 | 0B | 00 | 00 | 02 | CRC
Defrost | R | 0102000008 | 0002 | 0002 | CRC |  | RX: | 01 | 06 | 0B | 00 | 02 |  | CRC
Fast Freezing | R | 0102000008 | 0004 | 0004 | CRC
Keyboard | R | 0102000008 | 0008 | 0008 | CRC |  | WRITING 0 SECONDS AND 2 MINUTES
Energy Saving | R | 0102000008 | 0040 | 0040 | CRC
Humidity Fan | R | 0102220004 | 0001 | 0001 | CRC
Buzzer | R | 0102000008 | 0010 | 0010 | CRC
Holiday | R | 0102220004 | 0002 | 0002 | CRC
ALARMS
Error Pb1 | R | 0102080020 | 01000000 | 01000000 | CRC
Error Pb2 | R | 0102080020 | 02000000 | 02000000 | CRC
Error Pb3 | R | 0102080020 | 04000000 | 04000000 | CRC
Error Pb4 | R | 0102080020 | 08000000 | 08000000 | CRC
High Value Pb1 | R | 0102080020 | 10000000 | 10000000 | CRC
Low Value Pb1 | R | 0102080020 | 20000000 | 20000000 | CRC
High Value Pb2 | R | 0102080020 | 40000000 | 40000000 | CRC
Low Value Pb2 | R | 0102080020 | 80000000 | 80000000 | CRC
External Alarm | R | 0102080020 | 00010000 | 00010000 | CRC
Severe Alarm | R | 0102080020 | 00020000 | 00020000 | CRC
Open Door | R | 0102080020 | 00040000 | 00040000 | CRC
EEPROM Failure | R | 0102080020 | 00080000 | 00080000 | CRC
COMMANDS
Device ON | W | 050200FF00 |  |  | CRC
Device OFF | W | 0502000000 |  |  | CRC
Active Defrost | W | 050201FF00 |  |  | CRC
Alarm Mute | W | 050204FF00 |  |  | CRC
Fast Freeze ON | W | 050202FF00 |  |  | CRC
Fast Freeze OFF | W | 0502020000 |  |  | CRC
Keyboard LOCK | W | 050203FF00 |  |  | CRC
Keyboard UN-LOCK | W | 0502030000 |  |  | CRC
Energy saving ON | W | 050206FF00 |  |  | CRC
Energy saving OFF | W | 0502060000 |  |  | CRC
Light ON | W | 05021AFF00 |  |  | CRC
Light OFF | W | 05021A0000 |  |  | CRC
Aux ON | W | 05021CFF00 |  |  | CRC
Aux OFF | W | 05021C0000 |  |  | CRC
Humidity Fan ON | W | 050222FF00 |  |  | CRC
Humidity Fan OFF | W | 0502220000 |  |  | CRC
Holiday ON | W | 050223FF00 |  |  | CRC
Holiday OFF | W | 0502230000 |  |  | CRC
OUTPUT STATUS READING COMMANDS EXAMPLES:
DIGITAL OUTPUT MODBUS ADDRESSES MAPING:
[7 empty] | LIGHT |  | TX | 01 | 01 | 02 | 1A | 00 | 01 | CRC
[9 empty] | OFF | 01 | 01 | 01 | 00 |  |  | CRC
[9 empty] | ON | 01 | 01 | 01 | 01 |  |  | CRC
[7 empty] | DEFROST |  | TX | 01 | 01 | 02 | 17 | 00 | 01 | CRC
[9 empty] | OFF | 01 | 01 | 01 | 00 |  |  | CRC
[9 empty] | ON | 01 | 01 | 01 | 01 |  |  | CRC
[7 empty] | COMP. |  | TX | 01 | 01 | 02 | 1E | 00 | 01 | CRC
[9 empty] | OFF | 01 | 01 | 01 | 00 |  |  | CRC
[9 empty] | ON | 01 | 01 | 01 | 01 |  |  | CRC
[7 empty] | FAN |  | TX | 01 | 01 | 02 | 1B | 00 | 01 | CRC
[9 empty] | OFF | 01 | 01 | 01 | 00 |  |  | CRC
[9 empty] | ON | 01 | 01 | 01 | 01 |  |  | CRC
[7 empty] | ALARM |  | TX | 01 | 01 | 02 | 19 | 00 | 01 | CRC
[9 empty] | OFF | 01 | 01 | 01 | 00 |  |  | CRC
[9 empty] | ON | 01 | 01 | 01 | 01 |  |  | CRC
[7 empty] | DIG_IN. 2 |  | TX | 01 | 01 | 02 | 24 | 00 | 01 | CRC
[9 empty] | OFF | 01 | 01 | 01 | 00 |  |  | CRC
[9 empty] | ON | 01 | 01 | 01 | 01 |  |  | CRC

## MODBUS_PROTOCOL
DIXELL DEVICES SERIAL CONFIGURATION
Physical layer | RS485
Baud Rate | 9600 bps
Data Length | 8 bit
Parity | none
Stop Bit | 1
START/STOP | silent interval of 3 characters
MIN TIME BETWEEN TWO RETRY | 500 msec
Slave address
This field range is 1-247. Address 0 is used for the broadcast address. In this case all the slaves execute the command (only Write Holding Register command) but do not return any answer.
Exception codes
Dixell’s devices answers with exception codes when they are not able to execute the last command received. The exception configuration is:
Not implemented function (0x01)
In this case is requested a function that device is not able to support. Es: every time master sends a function different from ‘0x03’ or ‘0x10’
Not implemented area (0x02)
In this case is requested a resource absent in the device. Es: every time is requested a Logic Area absent.
Area index not valid (0x03)
In this case the value of the selected resource is out of range. Example:
· Every time is requested an Element of a Logic Area absent.
· More than 5 Elements requested.
· Writing a parameter out of range
· Writing in a Logic Area just reading.
Read/Write error (0x04)
The device didn’t succeeded in reading or writing requested operation. Es: every time reading or writing operation (Ram, E2, RTC and etc) is not ending correctly.
Busy state for slave active (0x06)
The device can’t execute requested operation because busy in another analogue operation. Master has to repeat the same request in another time.
The exception answer has the following format:
Slave address | Function code OR hex(80) | Exception code | CRC | CRC
|  |  | (LSByte) | (MSByte)
READING HOLDING REGISTER (0x03)
The command has the following format:
Slave Address | Function Code | Register Address | Register Address | Number of Registers | Number of Registers | CRC | CRC
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) | (LSByte) | (MSByte)
Slave Address: Defined the address of the device to read from.
Function Code: code of the desired function = 0x03
Register address: is the address of the first register to be red
Number of Registers: Defines the number of Elements (Register) that the device has to return (es. 3 = 3 Registers). No more than 5 Elements allowed.
CRC : Defined the CRC calculated for the frame data received and has to be used to verify the integrity of the data itself. It is calculated automatically (see page 7)
The answer message has the following format:
Slave address | Function code | NumByte | Byte Data 1 |  | Byte Data n | CRC | CRC
[6 empty] | (LSByte) | (MSByte)
NumByte: Defined the number of bytes followed without CRC.
ByteData: byte data buffer.
WRITE SINGLE REGISTER (0x06)
This command is not available for all instruments.
The command has the following format:
Slave Address | Function Code | Register Address | Register Address | DATA | DATA | CRC | CRC
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) | (LSByte) | (MSByte)
Slave Address: Defined the address of the device to write to.
Function Code: code of the desired function = 0x06
Register address: is the address of the register to write to
Data: is the data to write
CRC : Defined the CRC calculated for the frame data received and has to be used to verify the integrity of the data itself. It is calculated automatically (see page 7)
The answer message is an Eco of the sent command (so it has the same format)
WRITE MULTIPLE REGISTERS (0x10)
The command has the following format:
Slave address | Function Code | Register Address | RegisterAddress | Number of Registers | Number of Registers | NumByte | DATA | CRC | CRC
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) |  |  | (LSByte) | (MSByte)
Slave Address: Defined the address of the device to write to.
Function Code: code of the desired function = 0x10
Register address: is the address of the first register to write to
Number of Registers. : Defines the number of registers to write to. No more than 5 Elements allowed.
NumByte: Defined the number of bytes followed without CRC. The number of bytes has to be double respect the number of addressed Elements (NumByte = 2*Nreg).
CRC:
Defined the CRC calculated for the frame data received and has to be used to verify the integrity of the data itself. It is calculated automatically (see page 7).
The answer has the following format:
Slave Address | Function code | Register Address | Register Address | Number of Registers | Number of Registers | CRC | CRC
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) | (LSByte) | (MSByte)
CRC
The CRC value is calculated (on the entire message) by the transmitting device, which appends the CRC to the message. The receiving device recalculates a CRC during receipt of the message and compares the calculated value to the one received in the CRC field. If the two values are not equal, an error results.
Here there is the code (in C format) to generate CRC.
#define MODBUS_GENERATOR 0xA001
Unsigned int CRC;
void ModbusCalcCRC(unsigned char* Frame,unsigned char LenFrame)
{
unsigned char CntByte;
unsigned char j;
unsigned char bitVal;
CRC = 0xFFFF;
For(CntByte=0;CntByte<LenFrame;CntByte++)
{
CRC ^= Frame[CntByte];
for(j=0;j<8;j++)
{
bitVal = CRC & 0x0001;
CRC = CRC >> 1;
if(bitVal == 1)
CRC ^= MODBUS_GENERATOR;
}
}
}
NOTE:
To uniform interpretation mode of data, all data areas will have the following format:
SPECIAL COMANDS
READ BINARY STATUS : CODE 0x01
This commad consist in a reading of binary status heterogeneous collected in a byte sequence. The command must required maximum 80 binary elements (10 byte). The logic area assigned for this type of operation is 02.
COMMAND: the command have this following format
Slave Address | Function Code | Register Address | Register Address | Number of Registers | Number of Registers | CRC | CRC
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) | (LSByte) | (MSByte)
Byte | byte | Word | word | word
Adr Slave :
Address of the device to read e to
Function code :
Function code requested = 1.
Adr :
· MSByte: index logic area: always 2
· LSByte: : index of the first element to read (from 0 to max admitted)
N Reg :
Number of element (per bit) that the device must be answer (es. 3=3 bit , in a byte starting form bit0).
CRC (byte MS-LS):
defined the CRC calculated fro the frame data received and has to be used to verify integrity of the data itself
ANSWER : the answer have this format:
Adr | Function Code | NumByte | Byte |  | Byte | CRC
Slave |  |  | Dato 1 |  | dato n | (LSByte) (MSByte)
byte | byte | byte | byte |  | byte | word
NumByte: Number of byte data that following excluding the CRC
ByteDato: first field data each bite
WRITE SINGLE BINARY STATUS: CODE 0x05
This command can write a single binary status. The logic area is 02. The operation of bit SET or RESET is defined from the value of the field “DATO” in the following way : if the value is 0000H the bit will be RESET, if the value is 0FF00H the bit will be SET. Other different value will be no steer.
COMMAND: the command have this following format
Slave Address | Function Code | Register Address | Register Address | DATA | DATA | CRC | CRC
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) | (LSByte) | (MSByte)
Byte | byte | word | word | word
Adr Slave :
Address of the device to write to
Function code :
Function code requested = 5.
Adr :
· MSByte: index logic area: always 2
· LSByte: index of the binary element to write to.
DATO :
· 0000H : reset of the element
· 0FF00H : set of the element
CRC (byte MS-LS):
defined the CRC calculated fro the frame data received and has to be used to verify integrity of the data itself
ANSWER : the answer have this format:
Adr | Function Code | Adr | DATO | CRC
Slave |  | (MSByte) (LSByte) | (MSByte) (LSByte) | (LSByte) (MSByte)
byte | byte | word | word | word

## PARAMETERS
REGISTER ( dec)
769 | Hy | Differential | Regulation | byte | [0,1°C ÷ 25,5°C] [1°F ÷ 45°F]
770 | LS | Minimum set point | Regulation | word | [-100,0°C ÷ SET] [-148°F ÷ SET]
771 | US | Maximum set point | Regulation | word | [SET ÷ 150,0°C] [SET ÷ 302°F]
772 | ot | Thermostat probe calibration | Probes | byte | [-12,0°C ÷ 12,0°C] [-21°F ÷ 21°F]
773 | P2P | Evaporator probe presence | Probes | 1bit | n(0) - Y(1)
774 | oE | Evaporator probe calibration | Probes | byte | [-12,0°C ÷ 12,0°C] [-21°F ÷ 21°F]
775 | P3P | Third probe presence | Probes | 1bit | n(0) - Y(1)
776 | o3 | Third probe calibration | Probes | byte | [-12,0°C ÷ 12,0°C] [-21°F ÷ 21°F]
777 | P4P | Fourth probe presence | Probes | 1bit | n(0) - Y(1)
778 | o4 | Fourth probe calibration | Probes | byte | [-12,0°C ÷ 12,0°C] [-21°F ÷ 21°F]
779 | odS | Outputs delay at start up | Regulation | byte | 0 ÷ 255 (min.)
780 | AC | Anti-short cycle delay | Regulation | byte | 0 ÷ 50 (min.)
781 | AC1 | Second compressor start delay | Regulation | byte | 0 ÷ 255 (sec.)
782 | rtr | P1-P2 percentage for regulation | Regulation | byte | 0 ÷ 100 (100=P1 , 0=P2)
783 | CCt | Continuous cycle duration | Regulation | byte | 0 ÷ 24H0(144)
784 | CCS | Set point for continuous cycle | Regulation | word | [-100.0°C ÷ 150,0°C] [-148°F ÷ 302°F]
785 | Con | Compressor ON time with faulty probe | Regulation | byte | 0 ÷ 255 (min.)
786 | CoF | Compressor OFF time with faulty probe | Regulation | byte | 0 ÷ 255 (min.)
787 | CH | Kind of action: heating cooling | Regulation | 1bit | CL(0) - Ht(1)
788 | CF | Temperature measurement unit | Regulation | 1bit | °C(0) - °F(1)
789 | rES | Resolution | Regulation | 1bit | dE(0) - in(1)
790 | Lod | Probe displayed | Regulation | 4bit | P1(0) - P2(1) - P3(2) - P4(3) - SEt(4) - dtr(5)
791 | rEd | X-REP display | Regulation | 4bit | P1(0) - P2(1) - P3(2) - P4(3) - SEt(4) - dtr(5)
792 | dLy | Display temperature delay | Regulation | byte | 0 ÷ 20M0 (120) (10 sec.)
793 | dtr | P1-P2 percentage for display | Regulation | byte | 1 ÷ 99
794 | EdF | Defrost mode | Defrost | 1bit | rtC(0) - in(1)
795 | tdF | Defrost type | Defrost | 1bit | EL(0) - in(1)
796 | dFP | Probe selection for first defrost | Defrost | 4bit | nP(0) - P1(1) - P2(2) - P3(3) - P4(4)
797 | dSP | Probe selection for second defrost | Defrost | 4bit | nP(0) - P1(1) - P2(2) - P3(3) - P4(4)
798 | dtE | Defrost termination temperature first defrost | Defrost | word | [-55.0°C ÷ 50.0°C] [-67°F ÷ 122°F]
799 | dtS | Defrost termination temperature second defrost | Defrost | word | [-55.0°C ÷ 50.0°C] [-67°F ÷ 122°F]
800 | idF | Interval between defrost cycles | Defrost | byte | 0 ÷ 120 (ore)
801 | MdF | (Maximum) length for first defrost | Defrost | byte | 0 ÷ 255 (min.)
802 | MdS | (Maximum) length for second defrost | Defrost | byte | 0 ÷ 255 (min.)
803 | dSd | Start defrost delay | Defrost | byte | 0 ÷ 255 (min.)
804 | dFd | Displaying during defrost | Defrost | 2bit | rt(0) - it(1) - SEt(2) - dEF(3)
805 | dAd | Max display delay after defrost | Defrost | byte | 0 ÷ 255 (min.)
806 | Fdt | Draining time | Defrost | byte | 0 ÷ 255 (min.)
807 | dPo | First defrost after start-up | Defrost | 1bit | n(0) - Y(1)
808 | dAF | Defrost delay after fast freezing | Defrost | byte | 0 ÷ 24H0(144)
809 | FnC | Fan operating mode | Fan | 2bit | C_n(0) - O_n(1) - C_Y(2) - O_Y(3)
810 | Fnd | Fan delay after defrost | Fan | byte | 0 ÷ 255 (min.)
811 | FCt | Differential of temperature for forced activation of fans | Fan | byte | [0°C ÷ 50°C] [0°F ÷ 90°F]
812 | FSt | Fan stop temperature | Fan | word | [-55.0°C ÷ 50.0°C] [-67°F ÷ 122°F]
813 | Fon | Fan on time with compressor off | Fan | 4bit | 0÷15 (min.)
814 | FoF | Fan off time with compressor off | Fan | 4bit | 0÷15 (min.)
815 | FAP | Probe selection for fan | Fan | 4bit | nP(0) - P1(1) - P2(2) - P3(3) - P4(4)
816 | FSU | Kind of action of fan | Fan | 1bit | Std(0) - FoF(1) - Fon(2)
817 | ACH | Kind of action for auxiliary relay | Auxiliary | 1bit | CL(0) - Ht(1)
818 | SAA | Set point for auxiliary relay | Auxiliary | word | [-100.0°C ÷ 150,0°C] [-148°F ÷ 302°F]
819 | SHy | Differential for auxiliary relay | Auxiliary | byte | [0,1°C ÷ 25,5°C] [1°F ÷ 45°F]
820 | ArP | Probe selection for auxiliary relay | Auxiliary | 4bit | nP(0) - P1(1) - P2(2) - P3(3) - P4(4)
821 | Sdd | Auxiliary relay switched off during defrost | Auxiliary | 1bit | n(0) - Y(1)
822 | ALP | Probe selection for temperature alarms | Alarm | 4bit | nP(0) - P1(1) - P2(2) - P3(3) - P4(4)
823 | ALC | Temperature alarms configuration | Alarm | 1bit | rE(0) - Ab(1)
824 | ALU | Maximum temperature alarm | Alarm | word | °C[0.0° ÷ 50.0° o ALL ÷ 150,0°] °F[0° ÷ 90° o ALL ÷ 302°]
825 | ALL | Minimum temperature alarm | Alarm | word | °C[0.0° ÷ 50.0° o -100.0° ÷ ALU] °F[0° ÷ 90° o -148.0° ÷ ALU]
826 | AFH | Differential for temperature alarm recovery | Alarm | byte | [0,1°C ÷ 25,5°C] [1°F ÷ 45°F]
827 | ALd | Temperature alarm delay | Alarm | byte | 0 ÷ 255 (min.)
828 | dAo | Delay of temperature alarm at start up | Alarm | byte | 0 ÷ 24H0(144)
829 | AP2 | Probe selection for condenser temperature alarms | Alarm | 4bit | nP(0) - P1(1) - P2(2) - P3(3) - P4(4)
830 | AL2 | Condenser low temperature alarm | Alarm | word | [-100.0°C ÷ 150,0°C] [-148°F ÷ 302°F]
831 | AU2 | Condenser high temperature alarm | Alarm | word | [-100.0°C ÷ 150,0°C] [-148°F ÷ 302°F]
832 | AH2 | Differ. for condenser temp. alarm recovery | Alarm | byte | [0,1°C ÷ 25,5°C] [1°F ÷ 45°F]
833 | Ad2 | Condenser temperature alarm delay | Alarm | byte | 0 ÷ 255 (min.)
834 | dA2 | Delay of condenser temper. alarm at start up | Alarm | byte | 0 ÷ 24H0(144)
835 | bLL | Compressor off for condenser low temperature alarm | Alarm | 1bit | n(0) - Y(1)
836 | AC2 | Compressor off for condenser high temperature alarm | Alarm | 1bit | n(0) - Y(1)
837 | tbA | Alarm relay switched off by pushing a key | Alarm | 1bit | n(0) - Y(1)
838 | oA1 | First relay configuration | Configuration | 4bit | dEF(0) - FAn(1) - ALr(2) - LiG(3) - AUS(4) - OnF(5) - db(6) - CP2(7) - dF2(8) - HES(9)
839 | oA2 | Second relay configuration | Configuration | 4bit | dEF(0) - FAn(1) - ALr(2) - LiG(3) - AUS(4) - OnF(5) - db(6) - CP2(7) - dF2(8) - HES(9)
840 | oA3 | Third relay configuration | Configuration | 4bit | dEF(0) - FAn(1) - ALr(2) - LiG(3) - AUS(4) - OnF(5) - db(6) - CP2(7) - dF2(8) - HES(9)
841 | oA4 | Fourth relay configuration | Configuration | 4bit | dEF(0) - FAn(1) - ALr(2) - LiG(3) - AUS(4) - OnF(5) - db(6) - CP2(7) - dF2(8) - HES(9)
842 | AOP | Alarm relay polarity | Alarm | 1bit | OP(0) - CL(1)
843 | i1P | Digital input 1 polarity | Digital inputs | 1bit | OP(0) - CL(1)
844 | i1F | Digital input 1 configuration | Digital inputs | 4bit | dor(0) - dEF(1)
845 | i2P | Digital input 2 polarity | Digital inputs | 1bit | OP(0) - CL(1)
846 | i2F | Digital input 2 configuration | Digital inputs | 4bit | EAL(0) - bAL(1) - PAL(2) - dor(3) - dEF(4) - ES(5) - AUS(6) - Htr(7) - FAn(8) - HdF(9) - onF(10)
847 | did | Digital input 2 alarm delay | Digital inputs | byte | 0 ÷ 255 (min.)
848 | doA | Door alarm delay | Digital inputs | byte | 0 ÷ 255 (min.)
849 | nPS | Number of activation of pressure switch | Digital inputs | 4bit | 0 ÷ 15
850 | OdC | Compress and fan status when open door | Digital inputs | 2bit | no(0) - FAn(1) - CPr(2) - F-C(3)
851 | rrd | Regulation restart with door open alarm | Alarm | 1bit | n(0) - Y(1)
852 | HES | Differential for Energy Saving | Energy Saving | byte | [-30°C ÷ 30°C] [-54°F ÷ 54°F]
853 | Hur | Hour | Other | lock | sola lettura
854 | Min | Minutes | Other | lock | sola lettura
855 | dAY | Day of the week | Other | lock | sola lettura
856 | Hd1 | First day of week end | Regulation | 4bit | Sun(0) ÷ SAt(6) - nu(7)
857 | Hd2 | Second day of week end | Regulation | 4bit | Sun(0) ÷ SAt(6) - nu(7)
858 | iLE | Working days Energy saving start time | Energy Saving | byte | 0 ÷ 23h5 (143)
859 | dLE | Working days Energy saving duration | Energy Saving | byte | 0 ÷ 24h0 (144)
860 | iSE | Holyday Energy saving start time | Energy Saving | byte | 0 ÷ 23h5 (143)
861 | dSE | Holyday Energy saving duration | Energy Saving | byte | 0 ÷ 24h0 (144)
862 | Ld1 | 1st working days defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
863 | Ld2 | 2nd working days defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
864 | Ld3 | 3rd working days defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
865 | Ld4 | 4th working days defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
866 | Ld5 | 5th working days defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
867 | Ld6 | 6th working days defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
868 | Sd1 | 1st Holyday defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
869 | Sd2 | 2nd Holyday defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
870 | Sd3 | 3rd Holyday defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
871 | Sd4 | 4th Holyday defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
872 | Sd5 | 5th Holyday defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
873 | Sd6 | 6th Holyday defrost start time | Defrost | byte | 0 ÷ 23H5(143) - nu(144)
874 | Adr | Serial address | Other | byte | 1 ÷ 247
875 | PbC | Kind of probe | Probes | 1bit | Pt1(0) - ntC(1)
876 | OnF | On/off key configuration | Configuration | 2bit | nu(0) - OFF(1) - ES(2)
877 | LPC | Light key configuration | Configuration | 2bit | nu(0) - LiG(1) - AUS(2) - FHU(3)
878 | dPC | Defrost key configuration | Configuration | 1bit | dEF(0) - AUS(1)
879 | dP1 | Probe 1 value | Other | lock | (valore sonda)
880 | dP2 | Probe 2 value | Other | lock | (valore sonda)
881 | dP3 | Probe 3 value | Other | lock | (valore sonda)
882 | dP4 | Probe 4 value | Other | lock | (valore sonda)
883 | rSE | Real Set point (SET + ES + SETd) | Other | lock | sola lettura
884 | rEL | Firmware Release | Other | lock | sola lettura
885 | Ptb | Map code | Other | word | sola lettura
886 | SEt | Set point | Regulation | word | LS - US
900 | 384
EXAMPLES:
| HY | Tx: 01 03 03 01 00 01 D5 8E | read
| 2 | Rx: 01 03 02 00 14 B8 4B
| SET | Tx: 01 03 03 76 00 01 65 94 | read
| -5 | Rx: 01 03 02 FF CE 78 20
| 0 | Tx: 01 10 03 76 00 01 02 00 00 9E 6 | write
Rx: 01 10 03 76 00 01 E0 57
| hour | Tx: 01 03 03 55 00 01 94 5E | only read
| 23 | Rx: 01 03 02 00 17 F8 4A
Note on G24: * dtr = Visualizzazione percentuale
Note on G25: * dtr = Visualizzazione percentuale

## Sheet1
|  | Send | [5 empty] | Answer
Slave Address | Function code | Register Address | Register Address | Number of Registers | Number of Registers | CRC | CRC | Address | Function code | Number of Byte | Phase A |  |  | Phase B |  |  | Phase C |  |  | CRC LSB | CRC MSB
|  | (MSByte) | (LSByte) | (MSByte) | (LSByte) | (LSByte) | (MSByte) |  |  |  | Votage | Current | Power | Votage | Current | Power | Votage | Current | Power
C9 | 3 | 3 | 84 | 0 | 3 | 55 | EE | c9 | 03 | 24 | 0000089A | 0000000A | 000054B4 | 000008A1 | 0000000A | 5550 | 0000089E | 0000000A | 0000559E | XX | XX
Note on M4: jeqi: hex2dec(value)/10
Note on N4: jeqi: hex2dec(value)/10
Note on O4: jeqi: hex2dec(value)/100

## Sheet2
V |  | I |  | A
| 219.98 |  | 1 |  | 217.847
| 219.5 |  | 8 |  | 1755
| 219.06 |  | 16 |  | 3503
| 218.6 |  | 24 |  | 5245
| 218.1 |  | 32 |  | 6977

## Sheet3
C90324 | 0000089A | 0000000A | 000054B4 | 000008A1 | 0000000A | 5550 | 0000089E | 0000000A | 0000559E | 2202 | 10 | 21684 | 2209 | 10 | 21840 | 2206 | 10 | 21918
C90324 | 897 | 0000000A | 000054B4 | 000008A0 | 0000000A | 5550 | 0000089C | 0000000A | 0000559E | 2199 | 10 | 21684 | 2208 | 10 | 21840 | 2204 | 10 | 21918
C90324 | 0000089D | 0000000A | 000054B4 | 000008A5 | 0000000A | 5550 | 000008A1 | 0000000A | 0000559E | 2205 | 10 | 21684 | 2213 | 10 | 21840 | 2209 | 10 | 21918
C90324 | 0000089B | 0000000A | 000054B4 | 000008A3 | 0000000A | 5550 | 0000089E | 0000000A | 0000559E | 2203 | 10 | 21684 | 2211 | 10 | 21840 | 2206 | 10 | 21918
C90324 | 898 | 0000004E | 00029B44 | 000008A1 | 0000004E | 00029EEC | 0000089D | 0000004F | 00029FD6 | 2200 | 78 | 170820 | 2209 | 78 | 171756 | 2205 | 79 | 171990
C90324 | 899 | 0000004E | 00029B92 | 0000089F | 0000004E | 00029EEC | 0000089A | 0000004F | 00029FD6 | 2201 | 78 | 170898 | 2207 | 78 | 171756 | 2202 | 79 | 171990
C90324 | 895 | 0000004E | 00029B92 | 0000089D | 0000004E | 00029EEC | 899 | 0000004F | 00029FD6 | 2197 | 78 | 170898 | 2205 | 78 | 171756 | 2201 | 79 | 171990
C90324 | 899 | 0000004E | 00029B44 | 0000089F | 0000004E | 00029EEC | 0000089A | 0000004F | 00029FD6 | 2201 | 78 | 170820 | 2207 | 78 | 171756 | 2202 | 79 | 171990 | 1.0191
C90324 | 890 | 0000009D | 53292 | 899 | 0000009D | 53994 | 895 | 0000009D | 00053B1A | 2192 | 157 | 340626 | 2201 | 157 | 342420 | 2197 | 157 | 342810 | 1731.9067
C90324 | 895 | 0000009D | 53292 | 0000089D | 0000009D | 53994 | 898 | 0000009D | 00053B1A | 2197 | 157 | 340626 | 2205 | 157 | 342420 | 2200 | 157 | 342810
C90324 | 895 | 0000009D | 532 | 0000089B | 0000009D | 53994 | 896 | 0000009D | 00053B1A | 2197 | 157 | 1330 | 2203 | 157 | 342420 | 2198 | 157 | 342810
C90324 | 896 | 0000009D | 53292 | 0000089C | 0000009D | 53946 | 897 | 0000009D | 00053B1A | 2198 | 157 | 340626 | 2204 | 157 | 342342 | 2199 | 157 | 342810
C90324 | 892 | 000000EB | 0007C464 | 0000089A | 000000EB | 0007CE24 | 896 | 000000EC | 0007D0E2 | 2194 | 235 | 509028 | 2202 | 235 | 511524 | 2198 | 236 | 512226
C90324 | 891 | 000000EB | 0007C464 | 897 | 000000EB | 0007CE24 | 892 | 000000EC | 0007D094 | 2193 | 235 | 509028 | 2199 | 235 | 511524 | 2194 | 236 | 512148 | 17319.0625
C90324 | 0000088F | 000000EB | 0007C3C8 | 895 | 000000EB | 0007CD88 | 891 | 000000EC | 0007CFF8 | 2191 | 235 | 508872 | 2197 | 235 | 511368 | 2193 | 236 | 511992 | 17319.0625
C90324 | 891 | 000000EB | 0007C416 | 898 | 000000EB | 0007CD88 | 895 | 000000EC | 0007D046 | 2193 | 235 | 508950 | 2200 | 235 | 511368 | 2197 | 236 | 512070 | 8716.6667
C90324 | 0000088D | 0000013A | 000A55E8 | 895 | 0000013A | 000A6302 | 891 | 0000013B | 000A66AA | 2189 | 314 | 677352 | 2197 | 314 | 680706 | 2193 | 315 | 681642 | 80.0421
C90324 | 0000088E | 139 | 000A55E8 | 894 | 0000013A | 000A6302 | 0000088F | 0000013B | 000A66AA | 2190 | 313 | 677352 | 2196 | 314 | 680706 | 2191 | 315 | 681642
C90324 | 0000088C | 139 | 000A55E8 | 892 | 0000013A | 000A6302 | 0000088E | 0000013B | 000A665C | 2188 | 313 | 677352 | 2194 | 314 | 680706 | 2190 | 315 | 681564
C90324 | 0000088C | 0000013A | 000A559A | 893 | 0000013A | 000A62B4 | 890 | 0000013B | 000A665C | 2188 | 314 | 677274 | 2195 | 314 | 680628 | 2192 | 315 | 681564
| 89e | 0a | 5730 | 8a5 | 0a | 5780 | 8a2 | 0a | 57d0 | 2206 | 10 | 22320 | 2213 | 10 | 22400 | 2210 | 10 | 22480
| 896 | a0 | 55460 | 89d | a0 | 55b90 | 89a | a1 | 55d20 | 2198 | 160 | 349280 | 2205 | 160 | 351120 | 2202 | 161 | 351520
| 88d | 13f | a9b00 | 894 | 13f | aa870 | 890 | 141 | aab90 | 2189 | 319 | 695040 | 2196 | 319 | 698480 | 2192 | 321 | 699280
[10 empty] | 0 | 0 | 0.0038699 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 35980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219520
[9 empty] | 357f0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219120
[9 empty] | 35430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218160
[9 empty] | aab90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 699280
[9 empty] | aa820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698400
[9 empty] | a9a60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 694880
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sheet4
3861820
17650